## Sheet1
REG-03TFT COMMANDS LIST

COMMAND FORM:		<COMMAND>=<?><CR><LF> lub <VALUE><CR><LF>
TRANSMISSION DETAIL:		38400, PARITY NONE, 1N, 8BIT

NO	COMMAND	FORM	UNIT	RANGE	QUESTION	ADDITIONAL INFO	DESCRIPTION

1	R_ALL_SENSORS=	----	----	----	?	----	Question about sensor value
2	R_ALL_USER_SET=	----	----	----	?	----	Question about user settings
3	R_ALL_TIMER_SET=	----	----	----	?	----	Question about timere settings
4	R_ALL_SERVICE_SET=	----	----	----	?	----	Question about service settings
5	R_ALL_MAN_SET=	----	----	----	?	----	Question about manufacturer settings
6	R_ALL_LOGS=	----	----	----	?	----	Question about logs

7	R_SET_CH_TEMP=	xxx	°C	20-85/250/350	----	----	Set central heating temperature
8	R_SET_CH_PUMP=	xxx	°C	20-80/200/300	----	----	Set central heating pump temperature
9	R_SET_CH_HYST=	xxx	°C	2-30/50/100	----	----	Set central heating hysteresis
10	R_SET_MIN_CHTEMP=	xx	°C	15-60	----	----	Set central heating minimum temperature
11	R_SET_WUW_TEMP=	xx	°C	30-80	----	----	Set warm usage water temperature
12	R_SET_WUW_HYST=	xx	°C	1-25	----	----	Set warm usage water hysteresis
13	R_SET_WUW_PRIOR=	x	----	0-1	----	0-CH, 1-WUW	Set warm usage water priority
14	R_SET_WORK_POWER=	xxx	kW	15-500	----	----	Set burner work power
15	R_SET_MAINTAIN_POWER=	xx	kW	2-90	----	----	Set burner maintain/pause power
16	R_SET_BURNER_MODE=	x	----	0-2	----	0-normal, 1-stop&go, 2-analog	Set burner mode
17	R_SET_BEEP_SOUND=	x	----	0-1	----	0-off, 1-on	Set device sound (on/off)
18	R_SET_LANGUAGE=	x	----	0-1	----	0-PL, 1-EN	Set language

19	R_SET_FEEDER_PERFORMANCE=	xxx	kg/h	5-150	----	----	Set feeder performance
20	R_SET_FILLING_TIME=	xx	min	5-20	----	----	Set feeder filling time
21	R_SET_IGNITION_TIME=	xx	min	1-15	----	----	Set burner ignition time
22	R_SET_IGNITION_FAN=	xx	%	5-50	----	----	Set airfan power for ignition
23	R_SET_IGNITION_PELLET=	xxx	g	5-500	----	----	Set pellets quantity for ignition
24	R_SET_FAN_WORK=	x.xx	x	0.10-2.00	----	----	Set airfan overflow in working mode
25	R_SET_FAN_MAINTAIN=	x.xx	x	0.10-2.00	----	----	Set airfan overflow in maintain/pause mode
26	R_SET_STAB_IGNITION=	xxx	s	0-240	----	----	Set igniton stabilization
27	R_SET_STAB_MAINTAIN=	xxx	s	0-240	----	----	Set maintain/pause stabilization
28	R_SET_WORK_MOD=	x	x	1-5	----	----	Set working modulation
29	R_SET_MAINTAIN_MOD=	x.x	x	0.5-1.0	----	----	Set maintain/pause modulation
30	R_SET_MAX_MAINTAIN=	x	h	0-8	----	----	Set max maintain time
31	R_SET_CLEANING_TIME=	x	min	1-5	----	----	Set cleaning time
32	R_SET_ASH_WORK_TIME=	x	s	5-90	----	----	Set cleaning system working time
33	R_SET_ASH_IDLE_TIME=	x	s	1-60	----	----	Set cleaning system pause time
34	R_SET_FEEDER_INT_MULTI=	x.x	x	1.0-5.0	----	----	Set internal feeder multiplier
35	R_SET_FEEDER_PERIOD=	xx	s	10-60	----	----	Set feeder period
36	R_SET_FSENSOR_THRESHOLD=	xx	%	10-90	----	----	Set fire sensor detect threshold
37	R_SET_STB_TEMP=	xxx	°C	90-110/240/350	----	----	Set overheat temperature – STB (software)
38	R_SET_MODE=	x	----	0-1	----	0-off, 1-on	Set burner state (off/on)

39	R_SET_VERSION_CHECK=	x	----	0-1	----	----	Set configuration function – for reflash function
40	R_SET_REL1_OUT=	x	----	0-5	----	0-none, 1-stb, 2-wuw, 3-rake cleaning, 4-compressor cleaning, 5-rotate cleaning	Set REL1 output mode
41	R_SET_REL1_OUT=	x	----	0-4	----	0-none, 1-wuw, 2-rake cleaning, 3-compressor cleaning, 4-rotate cleaning	Set REL2 output mode
42	R_SET_TRIAC1_OUT=	x	----	0-2	----	0-none, 1-wuw, 2-internal feeder	Set TRIAC1 output mode
43	R_SET_SENS1_IN=	x	----	0-3	----	0-none, 1-room thermostat, 2-external control, 3-chimney temperature	Set SENS1 input mode
44	R_SET_SENS2_IN=	x	----	0-2	----	0-none, 1=wuw, 2-chimney temperature	Set SENS2 input mode
45	R_SET_CHSENS_TYPE=	x	----	0-2	----	0-KTY, 1-PT1000, 2-NTC	Set sensor type
46	R_SET_MIN_BPOWER=	xx	kW	10-90	----	----	Set minimum burner power
47	R_SET_MAX_BPOWER=	xxx	kW	20-500	----	----	Set maximum burner power

48	R_SET_TIME=	xxxxx	----	0-62359	----	day(x)+hour(xx)+minutes(xx)	Set current time
49	R_SET_TIMER0A=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Monday 0-12 hours
50	R_SET_TIMER0B=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Monday 12-23 hours
51	R_SET_TIMER1A=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Tuesday 0-12 hours
52	R_SET_TIMER1B=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Tuesday 12-23 hours
53	R_SET_TIMER2A=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Wednesday 0-12 hours
54	R_SET_TIMER2B=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Wednesday 12-23 hours
55	R_SET_TIMER3A=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Thursday 0-12 hours
56	R_SET_TIMER3B=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Thursday 12-23 hours
57	R_SET_TIMER4A=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Friday 0-12 hours
58	R_SET_TIMER4B=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Friday 12-23 hours
59	R_SET_TIMER5A=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Saturday 0-12 hours
60	R_SET_TIMER5B=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Saturday 12-23 hours
61	R_SET_TIMER6A=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Sunday 0-12 hours
62	R_SET_TIMER6B=	xxxxxxxx	----	0-11184810	----	0-timer off, 1-burner off, 2-lowering the temperature	Set Timer for Sunday 12-23 hours
63	R_SET_TIMER_STATE=	x	----	0-1	----	0-disable, 1-enable	Set Timer state (enable/disable)

64	R_CLEAR_USER_MEM=	x	----	0-1	----	1-reset	Reset user settings
65	R_CLEAR_USER_LOGS=	x	----	0-1	----	1-reset	Reset user logs
66	R_CLEAR_ALL_LOGS=	x	----	0-1	----	1-reset	Reset all logs
67	R_CLEAR_ALL_MEM=	x	----	0-1	----	1-reset	Reset all memory
68	R_REBOOT=	x	----	0-1	----	1-reset	Reboot a controller

69	R_SET_TEST_MODE=	x	----	0-1	----	0-test off, 1-test on	Set test (enable/disable)
70	R_SET_TEST_IGNITER=	x	----	0-1	----	0-off, 1-on	Set ignitor test (output off/on)
71	R_SET_TEST_AIRFAN	x	----	0-1	----	0-off, 1-on	Set airfan test (output off/on)
72	R_SET_TEST_FEEDER=	x	----	0-1	----	0-off, 1-on	Set feeder test (output off/on)
73	R_SET_TEST_CHPUMP=	x	----	0-1	----	0-off, 1-on	Set pump test (output off/on)
74	R_SET_TEST_RELAY1=	x	----	0-1	----	0-off, 1-on	Set REL1 test (output off/on)
75	R_SET_TEST_RELAY2=	x	----	0-1	----	0-off, 1-on	Set REL2 test (output off/on)
76	R_SET_TEST_TRIAC1=	x	----	0-1	----	0-off, 1-on	Set TRIAC1 test (output off/on)

77	R_VERSION=	xx.x	----	0.1-xx.x	----	----	Receive software version
78	R_SENSOR_EXT=	x	----	0-1	----	0-open contact, 1-close contact	Receive external sensor state
79	R_SENSOR_CH=	xxx.x	°C	-30-120/250/400	----	----	Receive central heating temperature
80	R_SENSOR_WUW=	xx.x	°C	-30-120	----	----	Receive warm usage water temperature
81	R_SENSOR_CHIMNEY=	xxx.x	°C	-30-400	----	----	Receive chimney temperature
82	R_SENSOR_FIRE=	xxx	%	0-100	----	----	Receive fire brightness
83	R_SENSOR_REF=	xx.x	°C	0-100	----	----	Receive reference temperature
84	R_SENSOR_BURNER=	x	----	0-1	----	0-alarm, 1-ok	Receive burner sensor state
85	R_FLAG_MODE=	xx	----	0-10	----	0-stop, 1-filling, 2-ignition, 3-cleaning, 4-working, 5-pause, 6-burning off, 7-standby, 8-no fuel, 9-burner overheat, 10-compressor	Receive burner mode state
86	R_FLAG_POWER=	xxx	----	0-500	----	----	Receive current burner power
87	R_FLAG_IGNITIONS=	x	----	1-3	----	----	Receive ignition count
88	R_FLAG_TIMER=	x	----	0-1	----	0-off, 1-on	Receive timer state
89	R_ALARM_FUEL=	x	----	0-1	----	0-ok, 1-no fuel	Receive fuel state
90	R_ALARM_BURNER=	x	----	0-1	----	0-ok, 1-burner alarm	Receive burner sensor state (overheat)
91	R_ALARM_STB=	x	----	0-1	----	0-ok, 1-STB alarm	Receive STB state
92	R_OUTPUT_IGNITER=	x	----	0-1	----	0-off, 1-on	Receive ignitor output state
93	R_OUTPUT_AIRFAN=	x	----	0-1	----	0-off, 1-on	Receive airfan output state
94	R_OUTPUT_AIRFAN_SP=	x	----	0-100	----	----	Receive airfan speed
95	R_OUTPUT_FEEDER_EXT=	x	----	0-1	----	0-off, 1-on	Receive external feeder output state
96	R_OUTPUT_FEEDER_INT=	x	----	0-1	----	0-off, 1-on	Receive internal feeder output state
97	R_OUTPUT_STB=	x	----	0-1	----	0-off, 1-on	Receive STB output state
98	R_OUTPUT_CHPUMP=	x	----	0-1	----	0-off, 1-on	Receive central heating pump output state
99	R_OUTPUT_WUWPUMP=	x	----	0-1	----	0-off, 1-on	Receive warm usage water pump output state
100	R_OUTPUT_CLEAN=	x	----	0-1	----	0-off, 1-on	Receive cleaning system output state
101	R_TIME=	xxxxx	----	0-62359	----	day(x)+hour(xx)+minutes(xx)	Receive current time
102	R_WARRANTY_M=	xx	----	0/1-12	----	0-no set date	Receive device start date (month)
103	R_WARRANTY_Y=	xx	----	0/18-99	----	0-no set date	Receive device start date (20year)